# PART 1 - GENERAL

1.1	RELATED SECTIONS:

Refer to Section 11600 for requirements relating to laboratory equipment including fume hoods.

Refer to Section 15050 for basic mechanical requirements.

Refer to Section 15150 for metering and instrumentation requirements.

Refer to Section 15190 for mechanical identification requirements.

Refer to Section 15250 for pipe, duct, and equipment insulation requirements.

Refer to Section 15400 for the requirements relating to plumbing.

Refer to Section 15500 for the requirements relating to heating, ventilating, and air conditioning material and equipment.

Refer to Section 15600 for the guidelines relating to the design of chilled water plants.

Refer to Section 15950 for the requirements relating to items for operating and controlling heating, ventilating, and air conditioning (HVAC) systems and equipment, including energy management and conservation systems (EMCS).

Refer to Section 15990 for the technical procedures for testing, adjusting, and balancing of mechanical equipment and systems, including the requirements relating to training University personnel in the operation of mechanical equipment.

Refer to Section 16150 for the requirements relating to electric motors.

1.2	SCOPE OF SECTION:

This section contains the requirements relating to air handling equipment (equipment used to move air through air distribution systems) and air distribution systems, including material and equipment for air distribution and ventilation.  Included are air terminal units (involving heat transfer and forced air supply), dampers, and design requirements for ventilation and outside air.

(Division 15 items are generally considered to be located within buildings and to extend a maximum distance of 5' outside of the building.)

1.3	GENERAL:

A.	DESIGN REQUIREMENT:

The air handling equipment and air distribution systems described within this section shall be designed by a North Carolina licensed professional engineer.

B.	INSULATION:

Air handling and distribution system components shall be externally insulated except as specifically indicated.

C.	OUTDOOR AIR REQUIREMENTS:

1.	A minimum of 20 CFM per person shall be provided to the occupied zone(s) of the building.  CO2 control shall be incorporated to maintain minimum acceptable indoor air quality.  Where applicable, outside air will be provided in accordance with the latest version of ASHRAE 62 for dilution ventilation. This outdoor air must be well mixed with return air in the mixed air plenum prior to conditioning and introduction into the supply duct.

2.	Modulated damper systems for outside air shall provide ASHRAE minimum outside air or 20 CFM per person (whichever quantity is greater) at all times.  Provide pre-heat coils or other appropriate active freeze protection.  Provide manual type freeze protection circuit to shut down fans and close outdoor air dampers.

3.	Refer to the paragraph on Air Outlets and Inlets at the end of this section for the requirements on outside air intakes.

D.	VENTILATION REQUIREMENTS:

1.	The building pressure differential must be slightly positive or neutral condition in relation to the outside atmosphere.

2.	Rooms or spaces utilized for lunch/break rooms, lounges, reprographics areas, kitchen areas, janitor closets, elevator equipment rooms, laundry rooms, and any other similar areas must be provided with exhaust air of adequate quantity.

3.	All spaces which are provided with exhaust ventilation must be maintained at a lower overall pressure (i.e. 0.01" w.g.) than the surrounding areas unless other balancing considerations take precedence.

4.	Any area which is designed to be exhausted must be isolated (disconnected) from the return air system.

5.	Local exhaust ventilation systems must be designed utilizing the latest version of the American Conference of Governmental Industrial Hygienists' Industrial Ventilation, a Manual of Recommended Practice.

6.	Exhaust stack discharge height must be in accordance with Chapter 5 of the American Conference of Governmental Industrial Hygienists' Industrial Ventilation, a Manual of Recommended Practice, latest version.

7.	Air exhausted by local exhaust system must be balanced with an appropriate amount of outside make-up from servicing air handling unit.

8.	Spaces which are provided with a local exhaust ventilation system must be provided with an interlock system between the exhaust fan controls and the make-up air system.

1.4	AIR HANDLING UNITS:

A.	GENERAL:

- The intent of this standard is to minimize required maintenance, provide access for maintenance, insure compatibility with central chiller plants, promote energy efficiency and provide long-lasting equipment.

- Designer to provide engineering calculations to Project Manager on size of unit selected.

- Interiors to be illuminated to 50 foot candles in fan, damper, filter, and coil sections for maintenance. Lighting fixtures in accessible service compartments shall be of non-corrosive materials, fluorescent lamp type, in vapor tight housing.  Each lighted compartment shall be switched separately.  Provide lighted toggle switches on AHU exterior.

- Mechanical equipment rooms shall be provided with hose bibbs and GFI convenience receptacles as needed for maintenance.  Where large AHUs require service from within AHU, provide appropriately located GFI convenience receptacles.  Lights, receptacles, and connected conduit shall be sealed airtight.

- Acceptable Manufacturers:  York, Trane, Carrier, or approved equal.

- Provide services of factory authorized service representative to perform start-up service.

- Test and adjust controls and safeties at the component level and as a system during installation and after start-up.

- Instruct University’s HVAC personnel in the operation, maintenance, and trouble-shooting of controls and safeties.  Fully demonstrate all operating sequences to University’s HVAC personnel.  This shall include normal and emergency/fail-safe operating sequences.

- Air handling units housing shall be designed to handle 1.5 times maximum anticipated operating pressure with less than 1% leakage of the design air volume.  Installed AHU assembly shall be isolated from external duct systems and pressure tested at maximum anticipated operation pressure and testing shall be witnessed by Engineer and Project Manager.  A certified field start-up test report shall be submitted to Engineer for review for compliance with project specifications.  Approved test report shall be submitted as part of the O&M manual.

- Fan inlets to have protective mesh screens.

- Belt guards to provide complete belt coverage with access slots/holes for use of contact type tachometer on rotating shafts of motors and fans.  Slots at motor end of belt guard shall allow testing at any position of motor on adjustment track.  Guards shall be readily removable for maintenance.

- Outdoor air wall louvers shall be sized to minimize water intake by keeping air intake velocities below 1000 fpm, drainable style, with bird screen of ½” mesh, extruded aluminum construction.  Louver blades to be at 45( angle.  Louver frame to be Kynar based finish, per designer’s color selection, and should match other building trim. Outdoor air plenums shall be fully accessible for inspection and maintenance and shall be sloped to drain outside or equipped with a pipe drain to an equipment room floor drain.

- Control dampers to be air foil shaped, low leakage type with vinyl edge seal and metal compression type jamb seal; opposed blade operation with maximum face velocity 1000 fpm.  Provide access doors, as large as needed to remove damper, for maintenance.

- Variable volume systems must be capable of providing 110% of design air volume at design static pressure.

- Constant volume systems must be provided with variable width motor sheeves for set-up and TAB servicer.  A preliminary TAB report shall be provided to the Engineer for review of compliance with project specifications.  An approved preliminary TAB report is required for contractor to procure final design ratio sheeves.  Once the fixed ratio sheeves are installed, a final TAB inspection shall be performed and subsequent TAB report generated and submitted for review to Engineer.

Approved final TAB report, indicated final fixed drive ratios, shall be included as part of HVAC O&M manual.

B.	ACCESS:

1.	Adequate clearance must be provided for all service, repairs and component replacement.  For new buildings, the unit should be placed such that the serviceman can freely walk to at least three sides of the unit.  For renovations the unit arrangement should be reviewed with Project Manager.

2.	All components (such as filters, motors, belts, and dampers) requiring regular service must be accessible and replaceable without disassembly of the unit.  Provide hinged access panels for filter and motor access.  Captive fasteners are acceptable for flat filter access.  Provide removable casing panels or access panels for coil and fan access.  Access doors for fan sections, and sections with dampers, shall be provided with 12” x 12” inspection windows.

C.	CASING:

1.	Casings shall be galvanized sheet steel with a minimum of 6 oz/ft² zinc.

2.	Units shall have double wall construction with a solid inner steel liner, galvanized, stainless, or approved coated.  Perforated steel liners shall only be used in fan sections for sound attenuation.  Steam cleaning shall be considered in material selection.

D.	INSULATION:

1.	Provide fiberglass insulation complying with NFPA 90A, a minimum of two inches thick and 3 pcf.

2.	All components, including zone damper sections, require insulation.  The unit shall not sweat.

E.	COILS:

- The tubes shall be copper with copper fins for biocidal benefits.  Maximum fin density is 10 fins per inch.

- Spray coils or electric heating coils are not allowed.

- Design chilled water coils for 16(F temperature rise minimum, or higher if requested by the Project Manager when connected to a central chiller plant.  Design for chilled water supply temperature available from the particular chiller plant at the building (typically 44(F).  Chilled water coil casings intermediate supports and coil support racks to be of 304 stainless steel construction.

- Design steam coils for 30 psig maximum working pressure.  Typical operating pressure is 12 psig.  Provide reducing stations as required.

- Provide preheat coils on all units with economizer systems and elsewhere as required for freeze protection.

- Provide a minimum of 30” of clearance at both the entering and exiting side of coil faces of both heating and cooling coils for steam cleaning access.  Access doors shall be full height.

- Interior surfaces in air handlers and duct systems shall be designed to accommodate mechanical cleaning, steam cleaning, and biocide treatment.

- All construction shall be double wall with access doors to each section for access to power clean both sides of the coils.

- Coil face air velocities must be limited to 500 fpm to limit moisture carry over.

F.	DRAIN PANS:

1.	Provide all welded 316 stainless steel, double wall, insulated drain pans that are sloped for positive drainage.  Provide drainage connections from bottom of pan, to eliminate ponding potential.  Drain pan shall not allow any standing water.

2.	Provide pans under coil, fan, and humidifier sections.

3.	Provide intermediate pans and copper drop tubes for stacked coils.

4.	Drain pans shall be drained by a trapped, insulated copper drainpipe that remains the full size (diameter) of the drain pan connection and indirectly drips into floor drain.  Provide “Tees” with clean out plugs and unions for maintenance of turns, traps, etc.

5.	Drain pans must be designed for easy access and maintenance.

6.	Drain pan shall begin 4” upstream of the coil face and extend continuously “h/2” feet downstream of the coil, where h = coil height in feet.

G.	FANS AND DRIVES:

1.	Air foil fans or backward curve fans are preferred.  Select fans for high efficiency.

2.	Provide premium efficiency motors rated for variable efficiency drives.  (Refer to Section 16150 for the requirements relating to electric motors.)

3.	Provide heavy duty belts and sheaves selected for a 1.5 safety factor. In multi-belt applications, use banded belts.  Drive assembly shall be dynamically balanced during start-up and a certified report provided to the Engineer for review and included in O&M manuals.

4.	Provide externally accessible lubrication fittings.

5.	Provide bearings with L-10 life of 200,000 hours.

6.	Provide spring type vibration isolation for ground floor rotating equipment.  For second floor and above rotating equipment, consider the use of concrete inertia pads with spring vibration isolation.

7.	Provide variable frequency drives on 5 Hp and larger motors.  Provide full size by-pass contactor.

H.	HUMIDIFIERS:  Refer to Section 15750.

I.	AIR FILTERS:

- Select final filters according to project requirements, but not less than 65% dust spot efficiency (ASHRAE Standard 52-76) for central station AHUs.  West Campus-use foam filters with biocide treatment.  Use linked poly panel filters for multiple filter slide-in applications.

- Provide extended surface prefilters of 25% dust spot efficiency.

- Provide delta-P gauges for all filter sections.

- Provide the manufacturer's information concerning pressure drop through the filters and recommended maintenance intervals necessary to prevent filter blow-out and clogging.

- Carbon filters are not allowed without written permission from Facilities Services.

- Filter cells must be sealed to prevent infiltration of by-pass air.

- Construction filters must be replaced during construction per filter manufacturer’s recommendation and before final inspection.  Provide a minimum of three (3) sets of filters.  One or more is used during construction activities.  The filters shall be changed just prior to final inspection and one (1) complete spare set shall be turned over to Facilities Services with other spare parts.

J.	CONTROLS:

1.	Provide all Energy Management and Conservation Systems (EMCS) monitoring and control points required by EMCS Standards.  Refer to Section 15950 for EMCS requirements.  The West campus EMCS is Johnson Controls-METASYS. The East campus is Siebe.

2.	Direct Digital Controls (DDC) are required.  Refer to Section 15950 for DDC requirements.

3.	Provide two-way chilled water control valves when units are served by campus central chiller plants.

4.	Building chilled water return temperature shall be optimized by monitoring AHU supply air temperature when requested by Facilities Services.

5.	Cooling coil controls shall be sequenced to accomplish dehumidification.

6.	Control space relative humidity to less than 60 percent.  Buildings with hardwood or of wood framing construction shall maintain relative humidity 35% (minimum) to 55% (maximum).

K.	INSTALLATION:

- Locate AHUs in mechanical rooms, never above ceilings.  Acoustically treat rooms and/or equipment to contain equipment noise.

- Mechanical rooms for AHUs must be full height.

- No rooftop AHUs are allowed without written permission from Facilities Services.

- Provide space for removing coils, fans, shafts, motors, etc.  Modification or demolition of other equipment or building structures shall not be required to allow equipment removal/replacement.  Show required service space on drawings.

- Mechanical rooms for AHUs shall be mechanically ventilated with outdoor air.

- Floor drains are not allowed in return air plenums.

- Mount AHUs on concrete housekeeping pads of suitable height to allow correct installation of condensate drain traps.  Minimum height is 4”.

- Provide a flow measuring device for each chilled water and heating hot water coil.

- Provide pressure taps (with cocks) and thermometers for each chilled water and heating hot water coil on both the supply and return.  Provide drains and air vents for all coils.

- DUCTWORK:

A.	GENERAL:

1.	All duct to be pressure tested at 1.5 times approximate maximum operating pressure prior to insulating.  Testing must be witnessed by Engineer and Project Manager.

2.	The cavity space above ceiling tiles and below the deck of the roof or floor above shall not be utilized as an air supply or return distribution plenum.  All air distribution shall be fully ducted.

3.	Ductwork utilized for supply and return air must have a hard surface with no internal lining, except as noted near fans.

- All duct systems must be constructed in a manner to be considered a sealed duct with a leakage rate of less than 2% of design cfm, measured at test pressure of 1.5 times maximum operating pressure.

- Duct distribution system must be designed and constructed to withstand test pressure.

B.	METAL DUCTWORK:

HVAC duct shall be fabricated from a minimum of 24 gauge galvanized sheet or stainless sheet steel or one gauge heavier than the SMACNA recommended duct gauge.  Flexible duct may be used only for short runs of 8' or less to air outlets.  Where lay-in type ceiling diffusers are used, it is preferred to have short runs of flexible duct, from 2’ to 8’, connecting the diffuser to hard duct system.  Flexible duct run outs shall be pulled tight, without any kinks, and supported with 2” wide banding to structure above to prevent any sagging.  Turns/bends greater than 45( shall be installed with hard round duct fittings.

C.	NONMETAL DUCTWORK:

Ductboard is not an acceptable material for ductwork.

D.	FLEXIBLE DUCTWORK:

Use of long runs of flexible duct with sharp bends is prohibited (i.e. greater than 8 feet and greater than 45().  The usage of round, hard duct run outs is encouraged to provide properly radiused offsets, turns, etc., and thereby limiting flexible duct installation failures.

Use multi-layered flexible duct with a “R” value of 6.0 or greater.

- DUCTWORK ACCESSORIES:

A.	DAMPERS:

Damper controls located on supply and return ducts that are utilized for balancing the system must be locked or fixed in place and marked with indelible ink or paint after final balance.

B.	DUCT ACCESS PANELS AND TEST HOLES:

Access doors shall be installed upstream for the inspection/cleaning of ductwork where dampers are located and at flow measuring stations, turning valves in sharp elbows, etc.  Access doors shall be sized 2” smaller than duct dimension (minimum) up to 24” X 24” (maximum).  Provide mechanical device identification on or adjacent to access door or test hole.

- AIR TERMINAL UNITS:

A.	GENERAL:

Terminal devices are intimately involved with thermal comfort and effective contaminant control.  The number, design, and location of these devices must be calculated by a NC licensed professional engineer.

B.	CONSTANT VOLUME:

C.	VARIABLE VOLUME:

1.	For Variable Air Volume (VAV) systems utilize terminal units of same construction as constant volume units.  No fan powered, filter style, fan coil units allowed.

- Provide high static pressure shutdown on variable volume units and blow-out duct rupture relief guards.

- ACCEPTABLE MANUFACTURERS:  Titus, Envirotech, Nailor Industries, or equal

- AIR OUTLETS AND INLETS:

A.	DIFFUSERS:

- Diffusers must be installed such that they are easily removed and replaced for cleaning and service.

- Troffer type diffusers at the diffuser/light fixture interface are prohibited.  Any system which is known to produce short circuiting between supply and return systems is prohibited.

- Diffusers (supply or return) shall not be located on the end of a duct run.  Branches are permitted near the end of a run.

- Branch run outs shall be provided with balancing dampers.  Diffusers shall not have balancing dampers.

- Diffusers in humid environments, such as pools, bathrooms, laundry rooms, and janitorial closets, shall be of all aluminum construction, off white finish.  All other diffusers shall be all steel construction, off white finish.

- All supply diffusers shall be insulated to prevent condensation.  Insulation to match that of duct system.

B.	OUTSIDE AIR INTAKES:

1.	Consideration must be given to the location of fresh air intakes to prevent introduction of pollutants to the building's air supply.  Maximal distance from pollutant sources is ideal. At minimum, fresh air intakes shall be at least 12 feet from all exhaust, & vent outlets (vertically and horizontally) and at least 10 feet above the ground. Loading docks, parking garages, and garbage storage areas shall be located at least 50 feet from any air intake (vertically or horizontally).

- Outside air intakes shall be protected from rain entrapment through the use of louvers, mist-eliminators or rain hoods.  Outside air intakes shall have integral bird and insect screening with openings between ¼ and ½ inch.

END OF SECTION