- PURPOSE

The purpose of this plan is to optimize energy conservation while maintaining adequately conditioned space.

- SYSTEM DESCRIPTION

The Austin Building is a three-story classroom and office building.  The HVAC system consists of three multi-zone air-handlers, a screw chiller and tube and shell hot water converter.  The heating and cooling is a four-pipe system with one cooling and one heating system.

- AIR HANDLING UNITS

AHU#	RM#	Area Supplied	Area Description

AHU-1	basement	1st floor	offices & classrooms

AHU-2	1st floor	2nd floor	offices & classrooms

AHU-3	2nd floor	3rd floor	offices & classrooms

- HVAC CONTROLS

  - SEQUENCE OF OPERATION

The HVAC system is controlled by an Invensys Ultivist control system.

    - AHU-1, 2 & 3 are multi-zone air-handlers with a hot water and chill water coils.

    - Pneumatic thermostats control each zone.

    - Deck temperature controls are based on outdoor air temperature and/or return air temperature.

    - Each AHU is equipped with minimum outdoor air with preheat and has a freezestat for freeze protection.

    - Each AHU is equipped with fire alarm protection to shut down unit in case of an alarm.

  - LOAD MANAGEMENT

The chill water system resets supply water temperature on load shed.  This reset is 2 degrees higher before 4:00pm and 4 degrees higher after 4:00pm.

- COOLING SYSTEM

The building is cooled with a Carrier screw chiller.  The on rise of outdoor air temperature the BAS starts the chill water pumps and enables the chiller.  When the chiller see the load it starts the condenser pumps, enables the cooling tower and starts the chiller.

- HEATING SYSTEM

A tube and shell converter provides the reheat for the perimeter heat with a circulator pump staged by outdoor air temperature.  The BAS adjusts the temperature reset based on outdoor air temperature.

- SPECIAL OPERATING INSTRUCTIONS

1st floor east wing is a computer center with 2 Liebert split systems, 1 Trane split system for the computer area.  The office area of the computer area is conditioned by a York split system.  None of the computer area is on the BAS system.