- PURPOSE

The purpose of this plan is to optimize energy conservation while maintaining adequately conditioned space.

- SYSTEM DESCRIPTION

Harold H. Bate Building (formerly known as the General Classroom Building or GCB) is a three-story classroom building.  One air-handling unit with perimeter heat serves the building. The building’s chilled and hot water circulates using a four-pipe system with one chilled water system and one hot water system.

- AIR HANDLING UNITS

AHU#	RM#	Area Supplied	Area Description

1        		Main Mechanical Room	Entire Building

- HVAC CONTROLS

  - SEQUENCE OF OPERATION

The HVAC system is controlled by an Invensys Ultavist control system.

    - AHU 1 has a constant temperature supply which feeds VAV boxes in each room.  Pneumatic thermostats in each area control the VAV boxes.  Supply air temperature is reset based on return air temperature.

    - Pneumatic thermostats control the perimeter heat boxes.  The heat is supplied by the hot water system located in the main mechanical room.

    - Additional cooling is done for the computer labs on the third floor by two Liebert units.

  - LOAD MANAGEMENT

The chill water system resets supply water temperature on load shed.  This reset is 2 degrees higher before 4:00pm and 4 degrees higher after 4:00pm.

- COOLING SYSTEM

The building is cooled with chilled water, using two McQuay screw chillers.  The chillers are set up to stage by load demand and outdoor air temperature.

- HEATING SYSTEM

  - A tube and shell converter provides the reheat for the perimeter heat with two circulator pumps staged by outdoor air temperature.  Temperature reset is utilized based on outdoor air temperature.

  - A steam coil provides heat for AHU 1 to maintain supply air temperature.

- SPECIAL OPERATING INSTRUCTIONS

  - Economizer operation:

Outdoor air dampers modulate to maintain supply air temperature between 30 degrees and 60 degrees.  And go to a minimum position (15% open) between 60 degrees and 90 degrees.

  - Carbon dioxide damper operation (economizer override):

If the carbon dioxide levels approach the 900ppm level the outside air dampers will modulate open to lower the level if outdoor air temperatures are between 30 degrees and 90 degrees.

  - AHU 1 static control:

The inlet vanes on the two supply air fans and the one return air fan modulate to maintain the predetermined static pressure.