- PURPOSE

The purpose of this plan is to optimize energy conservation while maintaining adequately conditioned space.

- SYSTEM DESCRIPTION

The Brewster Building is four buildings (A, B, C & D) sharing utilities. “A-wing” is four-story buildings, which is primarily offices.  “B, C & D-WINGS”, are three story buildings, which are primarily classrooms.  There are 13 air-handling units served by a four pipe chill-hot water system.

- AIR HANDLING UNITS

AHU#	RM#	Area Supplied	Area Description

A-1	A-wing 1st floor	A-wing 1st floor 		Offices

A-2	A-wing 2nd floor	A-wing 2nd floor		Offices

A-3	A-wing 3rd floor 	A-wing 3rd floor		Offices

A-4	A-wing 4th floor	A-wing 4th floor		Offices

B-1	B-wing 1st floor	B-wing 1st floor		Classrooms

B-2	B-wing 2nd floor	B-wing 2nd floor 		Classrooms

B-3	B-wing 3rd floor	B-wing 3rd floor 		Classrooms

C-1	C-wing 1st floor	C-wing 1st floor 		Classrooms

C-2	C-wing 2nd floor	C-wing 2nd floor 		Classrooms

C-3	C-wing 3rd floor	C-wing 3rd floor 		Classrooms

D-1	D-wing 1st floor	D-wing 1st floor 		Classrooms

D-2	D-wing 2nd floor	D-wing 2nd floor 		Classrooms

D-3	D-wing 3rd floor	D-wing 3rd floor 		Classrooms

- HVAC CONTROLS

## SEQUENCE OF OPERATION

HVAC Control

The HVAC system is controlled by an Invensys Ultavist control system.

    - The four AHU’s in A-wing are multizone units with three zones on each floor.

    - The AHU’s in B, C & D Wings is a dual duct system with VAV boxes in each area.

    - All Thermostats for each of the zones or VAV boxes are pneumatically controlled.

    - Deck temperature controls are reset based on outdoor air and building load.

## LOAD MANAGEMENT

## The chill water system resets supply water temperature on load shed.  This reset is 2 degrees higher before 4:00pm and 4 degrees higher after 4:00pm.

# COOLING SYSTEM

The building is cooled with a 350 ton Trane centrifugal chiller. The chill water pump is started and the chiller enabled by outdoor air.  The chiller then controls itself based on water temperature.  The cooling tower has a variable speed fan to control the condenser water temperature.

- HEATING SYSTEM

A tube and shell converter provides the reheat for the perimeter heat with two circulator pumps staged by outdoor air temperature.  Temperature reset is utilized based on outdoor air temperature.

- SPECIAL OPERATING INSTRUCTIONS

The A-wing AHU’s are zoned units which mix air to desired supply air temp, while the B, C & D-wing AHU’s are constant static dual duct systems to supply VAV boxes in each area.  All of the AHU’s incorporate the use of economizers for energy savings.