- PURPOSE

The purpose of this plan is to optimize energy conservation while maintaining adequately conditioned space.

- SYSTEM DESCRIPTION

The Carol Belk Allied Health building is a three-story classroom building served by three dual duct air-handlers.  The system utilizes a four-pipe system with an air-cooled chiller and on site boiler.

- AIR HANDLING UNITS

AHU#	RM#			Area Supplied	Area Description

AHU-1	1ST floor mechanical	1st floor 		offices & classrooms

AHU-2	2nd floor mechanical	2nd floor		offices & classrooms

AHU-3	3rd floor mechanical	3rd floor		offices & classrooms

- HVAC CONTROLS

  - SEQUENCE OF OPERATION

The HVAC system is controlled by an Invensys DMS-3500 system, connected to the Ethernet and an Ultivist operator workstation at the Steam Plant for control and alarm monitoring.

    - AHU1, 2 & 3 are dual duct, constant pressure air-handlers.  They incorporate a chill water and hot water coil to maintain temperature on the hot and cold decks.

    - Full economizer operation is used between 30 degrees and 60 degrees.  Minimum fresh air is introduced between 60 degrees and 90 degrees.

    - Each air-handler is equipped with freeze protection and fire protection to stop the blowers and close the outdoor dampers.

    - Cold decks on the air-handlers are on outdoor air reset for energy savings.

    - Hot decks do not have control valves and relay on the hot water reset for hot deck control.

    - The dual duct air-handlers supply VAV boxes in each area.  Pneumatic thermostats control these VAV boxes.  (Boxes cannot be accessed due to asbestos in the ceiling.)

    - The stand alone boiler uses an outdoor air reset to change water temperature for energy savings.

  - LOAD MANAGEMENT

The chill water system resets supply water temperature on load shed.  This reset is 2 degrees higher before 4:00pm and 4 degrees higher after 4:00pm.

- COOLING SYSTEM

The building is cooled with chill water using a McQuay air-cooled screw chiller.  Two chill water pumps located in the 1st floor mechanical room circulate the chilled water.

- HEATING SYSTEM

A stand-alone gas fired boiler is used for the heating hot water system.  An outdoor thermostat enables the boiler and water temperature is reset by outdoor air temperature.

- SPECIAL OPERATING INSTRUCTIONS