- PURPOSE

The purpose of this plan is to optimize energy conservation while maintaining adequately conditioned space.

- SYSTEM DESCRIPTION

Fleming Residence Hall is a two-story dormitory.  The HVAC system consists of 12 air-handlers, a four-pipe heating/cooling system.

- AIR HANDLING UNITS

AHU#	RM#	Area Supplied	Area Description

AHU-1                basement east	 	dorm rooms

AHU-2                basement east	  	dorm rooms

AHU-3                basement north	 	dorm rooms

AHU-                  basement north	 	dorm rooms

AHU-5                basement west		dorm rooms

AHU-6                basement west		dorm rooms

AHU-7                   attic east		dorm rooms

AHU-8	   attic east		dorm rooms

AHU-9	   attic north		dorm rooms

AHU-10	   attic north		dorm rooms

AHU-11	   attic west		dorm rooms

AHU-12	   attic west		dorm rooms

- HVAC CONTROLS

  - SEQUENCE OF OPERATION

The HVAC system is controlled by an Invensys DMS-3500 system connected to the Ethernet and an Ultivist operator workstation at the Steam Plant for control and alarm monitoring.

    - All 12 air handling units are mixed air single path with 2 thermostats in the space.  They use hot water and chilled water coils.  All of the coils have freeze protection.  There is a fire alarm shutdown to all of the fans and dampers.  The BAS system controls the air-handlers by averaging the space temperatures of the 2 thermostats.

    - There are 5 exhaust fans, which exhaust the trash rooms and restrooms.

  - LOAD MANAGEMENT

There is no load management in this building.

- COOLING SYSTEM

The building is cooled with chill water, using an air-cooled chiller located outside of the building.  The chiller and chill water pumps are controlled by the BAS.

- HEATING SYSTEM

A tube and shell converter provides the heat with two circulator pumps staged by outdoor air temperature.  Temperature reset is utilized based on outdoor air temperature. This system is controlled by the BAS.

- SPECIAL OPERATING INSTRUCTIONS