- PURPOSE

The purpose of this plan is to optimize energy conservation while maintaining adequately conditioned space.

- SYSTEM DESCRIPTION

The Fletcher Music Center is a three story classroom building with an attached recital hall.  There are 4 air handling units that utilize a four pipe chilled water and hot water system.

- AIR HANDLING UNITS

AHU#	RM#	Area Supplied	Area Description

1		main mechanical	1,2&3 floor	classrooms & offices

2A		“band room A” mechanical	band room A	classroom

2B		“band room B” mechanical	band room B	classroom

3		Recital hall mechanical 	Recital Hall	auditorium $ lobby

- HVAC CONTROLS

  - SEQUENCE OF OPERATION

HVAC Control

The HVAC system is controlled by an Invensys Ultavist control system.

    - Air-handler 3 is a multizone unit.

    - Air-handler 1 is a dual duct system supplying VAV boxes.

    - Air-handlers 2A & 2B are mixed air single path controlled by return air sensors.

    - All Thermostats for each of the zones or VAV boxes are pneumatically controlled.

    - Deck temperature controls are reset based on outdoor air and building load.

  - LOAD MANAGEMENT

The chill water system resets supply water temperature on load shed.  This reset is 2 degrees higher before 4:00pm and 4 degrees higher after 4:00pm.

- COOLING SYSTEM

The building is cooled with a 200 ton Carrier centrifugal chiller. The chill water pump is started and the chiller enabled by outdoor air.  The chiller then controls itself based on water temperature.  The cooling tower has a two-speed fan to control the condenser water temperature.

- HEATING SYSTEM

A tube and shell converter provides the reheat for the perimeter heat with two circulator pumps staged by outdoor air temperature.  Temperature reset is utilized based on outdoor air temperature.

- SPECIAL OPERATING INSTRUCTIONS