- PURPOSE

The purpose of this plan is to optimize energy conservation while maintaining adequately conditioned space.

- SYSTEM DESCRIPTION

Graham Building is three story classroom and office building.

- AIR HANDLING UNITS

AHU#	RM#	Area Supplied

AHU-1	1st floor mechanical	1st floor

AHU-2	2nd floor mechanical	2nd floor

AHU-3	3rd floor mechanical	3rd floor

- HVAC CONTROLS

  - SEQUENCE OF OPERATION

The HVAC system is controlled by an Invensys DMS-3500 system, connected to the Ethernet and an Ultivist operator workstation at the Steam Plant for control and alarm monitoring.

    - AHU-1, 2 & 3 are dual duct air-handlers serving mixing boxes located in the ceiling.  The air-handlers utilize chill water and hot water coils.

    - AHU-1, 2 & 3 use deck temperature sensors to maintain supply air temperature.  These controls are pneumatic and not monitored on the BAS.

- LOAD MANAGEMENT

There is no load management on this building.

- COOLING SYSTEM

The cooling is achieved through an air-cooled chiller located on the south side of the building.  The chiller is controlled and monitored by the BAS.

- HEATING SYSTEM

A tube and shell steam converter and hot water circulator pump achieve the hot water for the heating system.  The hot water system is not monitored by the BAS.

- SPECIAL OPERATING INSTRUCTIONS