- PURPOSE

The purpose of this plan is to optimize energy conservation while maintaining adequately conditioned space.

- SYSTEM DESCRIPTION

The Howell Science Building consists of three towers and an animal facility.  The HVAC system consists of seven single path air-handlers that supply VAV boxes, one single path air-handler, two screw chillers and four tube and shell hot water converters.  The heating and cooling is a four-pipe system with one cooling and one heating system.

- AIR HANDLING UNITS

AHU#	RM#	Area Supplied	Area Description

AHU-1	south basement	1st floor south	offices & classrooms

AHU-2	south penthouse	south tower	offices & classrooms

AHU-3	south penthouse	south tower	offices & classrooms

AHU-4	east penthouse	east tower	offices & classrooms

AHU-5	east penthouse	east tower	offices & classrooms

AHU-6	north penthouse	north tower	offices & classrooms

AHU-7	north penthouse	north tower	offices & classrooms

AHU-8	B-103	lecture room	classroom

- HVAC CONTROLS

  - SEQUENCE OF OPERATION

The HVAC system is controlled by an Invensys Ultavist control system.

    - AHU-1-7 are single zone air handlers supplying VAV boxes

    - AHU-8 is single path air handlers with hot water and chill water coils.

    - Pneumatic thermostats control the individual VAV boxes.

    - Deck temperature controls are based on outdoor air temperature and/or return air temperature.

    - Each AHU is equipped with minimum outdoor air with preheat and has a freezestat for freeze protection.

    - Each AHU is equipped with fire alarm protection to shut down unit in case of an alarm.

- LOAD MANAGEMENT

The chill water system resets supply water temperature on load shed.  This reset is 2 degrees higher before 4:00pm and 4 degrees higher after 4:00pm.

- COOLING SYSTEM

The building is cooled with two York screw chillers.  On the rise of outdoor air temperature the BAS starts the chill water pumps and enables the chiller.  When the chiller sees the load it starts the condenser pumps, enables the cooling tower and starts the chiller.

- HEATING SYSTEM

Four tube and shell converters provides hot water for heat with a circulator pump staged by outdoor air temperature.  The BAS adjusts the temperature reset based on outdoor air temperature.

- SPECIAL OPERATING INSTRUCTIONS