- PURPOSE

The purpose of this plan is to optimize energy conservation while maintaining adequately conditioned space.

- HVAC OPERATING SCHEDULE

The following schedule represents the time that each air-handling unit (AHU) shall condition its corresponding space:

AHU	SCHEDULE

All	** 24hrs/day, 7 days/week **

- ENERGY OPERATING DESCRIPTION

  - Biotech Building – Description

The Biotech building is a 2-story building which houses the Pediatric Outpatient Center on the first floor, and the Biotechnology Research department on the second floor. The building is approximately 28,152 sq ft and is served by 2 air handling units. There are also 4 additional steam space heaters.

  - HVAC Supply

# AHU#		Location 		Area Served

AHU-1	Ground Floor Mech	1st Floor Area

AHU-2	Ground Floor Mech	Ground Floor Pediatrics

  - HVAC Control

The HVAC system is controlled by pneumatic thermostats and is connected to the Johnson Controls Metasys System.

    - Thermostats

All AHU’s are controlled by pneumatic thermostats, which are located in the controlled and conditioned area.

    - Set Points

Set points are adjustable at the pneumatic thermostat.

    - Unoccupied Temperature Setback

These units are not currently equipped with any unoccupied features since they run 24hrs/day, 7 days/week.

    - Deck Control

These units are not equipped with hot deck/cold deck control, but do have VAV capabilities with reheat.

  - Chilled Water Supply

The building is cooled with chilled water, supplied by the Central Steam Plant. There is a lead/lag pump system for circulating the chilled water system to the air-handling units. The pumps are controlled by variable speed drives using the differential pressure of the chilled water loop as the control variable.

  - Heating Water Supply

The building is heated with steam provided by the Central Steam Plant.

  - Special Operations/Instructions

This building is served by a Generator, which supplies power during power outages and during peak shaving.