- PURPOSE

The purpose of this plan is to optimize energy conservation while maintaining adequately conditioned space.

- HVAC OPERATING SCHEDULE

The following schedule represents the time that each air-handling unit (AHU) shall condition its corresponding space:

AHU	SCHEDULE

All	** 24hrs/day, 7 days/week **

- ENERGY OPERATING DESCRIPTION

  - Laupus Health Science Library – Description

The Laupus Health Science Library is a 3-story building which houses the Library for the Health Sciences Campus. The building is approximately 480,279 sq ft and is served by 2 air handling units. There are no additional steam space heaters.

  - HVAC Supply

AHU#		Location 		Area Served

AC-3		GL-02			Library & Front Lobby

88-1		3rd Floor Mech	Office Area above Library

  - HVAC Control

The HVAC system is controlled by pneumatic thermostats and is connected to the Johnson Controls Metasys System.

    - Thermostats

All AHU’s are controlled by pneumatic thermostats, which are located in the controlled and conditioned area.

    - Set Points

Set points are generally non-adjustable at the pneumatic thermostat and are set at 73 degf.

    - Unoccupied Temperature Setback

These units are not equipped with any unoccupied features since they run 24hrs/day, 7 days/week.

    - Deck Control

These units are not equipped with hot deck/cold deck control, but have VAV capabilities with reheat.

  - Chilled Water Supply

The building is cooled with chilled water, supplied from the Central Steam Plant. There is a lead/lag pump system for circulating the chilled water system to the air handling units. The pumps are controlled by variable speed drives using the differential pressure of the chilled water loop as the control variable.

  - Heating Water Supply

The building is heated with steam provided by the Central Steam Plant. A reset schedule for the VAV reheat is based on outside air temp is utilized for energy efficiency. This schedule ranges from 110 degf at 80 degf outside, to 180 degf at 10 degf outside air.

  - Special Operations/Instructions

This building is served by the main Generator bank, which supplies power during power outages and during peak shaving.