- PURPOSE

The purpose of these plans is to optimize energy conservation while maintaining adequately conditioned space.

- HVAC OPERATING SCHEDULE

The following schedule represents the time that each air-handling unit (AHU) shall condition its corresponding space:

AHU	SCHEDULE

All	** 24hrs/day, 7 days/week **

- ENERGY OPERATING DESCRIPTION

- Life Sciences Building formerly known as Vivarium

  - Vivarium – Description

The Vivarium building is a single story building which houses animal research facilities, labs and housing. The building is approximately 15,090 sq ft and is served by 4 air handling units. There is also 1 additional steam space heater.

  - HVAC Supply

AHU#		Location 		Area Served

AHU-2	Mech Room		Office Area

ASA-1		Mech Room		Animal Area

ASA-2		Mech Room		Animal Area

ASA-3		Mech Room		Animal Area

- HVAC Control

The HVAC system is controlled by pneumatic thermostats and is connected to the Johnson Controls Metasys System.

  - Thermostats

All AHU’s are controlled by pneumatic thermostats, which are located in the controlled and conditioned area.

  - Set Points

Set points are non-adjustable at the pneumatic thermostat, but are adjusted in the Johnson Controls Metasys System.

  - Unoccupied Temperature Setback

These units are not equipped with any unoccupied features since they run 24hrs/day, 7 days/week.

  - Deck Control

AHU-2 is equipped with hot deck/cold deck capacity. The other units are not equipped with hot deck/cold deck control, but have VAV capabilities.

- Chilled Water Supply

The building is cooled with chilled water, supplied by the Central Steam Plant. There is a lead/lag pump system for circulating the chilled water system to the air handling units. The pumps are controlled by variable speed drives using the differential pressure of the chilled water loop as the control variable.

- Heating Water Supply

The building is heated with steam provided by the Central Steam Plant. A reset schedule for the VAV reheat is based on outside air temp is utilized for energy efficiency. This schedule ranges from 110 degf at 80 degf outside, to 180 degf at 10 degf outside air.

- Special Operations/Instructions

This building is served by a Generator, which supplies power during power outages and during peak shaving. The generator is being phased out, however, in favor of using the generator for the Warren Life Sciences Bldg.

- Warren Life Sciences Building

  - Warren Life Sciences Building – Description

The Warren Life Sciences building is a 2-story building which houses the animal research facilities, labs and housing. The building is approximately 75,392 sq ft and is served by 6 air handling units. There are also 8 additional steam space heaters.

  - HVAC Supply

AHU#		Location 		Area Served

AHU-1	1st Floor Mech	1st Floor Animal Holding

AHU-2	1st Floor Mech	1st Floor Rodent Area

AHU-3	Skyway Mech	1st Floor Office Area

AHU-4	2nd Floor Mech	2nd Floor

AHU-5	Skyway Mech	Skyway West

AHU-6	Penthouse Mech	Skyway East

  - HVAC Control

The HVAC system is controlled by electronic thermostats and is connected to the Johnson Controls Metasys System.

- Thermostats

All AHU’s are controlled by electronic thermostats, which are located in the controlled and conditioned area.

- Set Points

Set points are not adjustable at the thermostat, but are adjusted through the Johnson Controls Metasys System.

- Unoccupied Temperature Setback

These units are not equipped with any unoccupied features since they run 24hrs/day, 7 days/week.

- Deck Control

These units are not equipped with hot deck/cold deck control, but have VAV capabilities.

  - Chilled Water Supply

The building is cooled with chilled water, supplied by the Central Steam Plant. There is a lead/lag pump system for circulating the chilled water system to the air handling units. The pumps are controlled by variable speed drives using the differential pressure of the chilled water loop as the control variable.

  - Heating Water Supply

The building is heated with steam provided by the Central Steam Plant. A reset schedule for the VAV reheat is based on outside air temp is utilized for energy efficiency. This schedule ranges from 110 degf at 80 degf outside, to 180 degf at 10 degf outside air.

  - Special Operations/Instructions

This building is served by a Generator, which supplies power during power outages and during peak shaving.