- PURPOSE

The purpose of this plan is to optimize energy conservation while maintaining adequately conditioned space.

- HVAC OPERATING SCHEDULE

The following schedule represents the time that each air-handling unit (AHU) shall condition its corresponding space:

AHU	SCHEDULE

All	** 24hrs/day, 7 days/week **

- ENERGY OPERATING DESCRIPTION

  - Leo Jenkins Cancer Center – Description

The Leo Jenkins Cancer Center building is a 2-story building that serves as a Cancer treatment center. The building is approximately 39,155 sq ft and is served by 2 air-handling units. There are also 2 additional steam space heaters.

  - HVAC Supply

AHU#		Location 		Area Served

AC-8		1st Floor Mech	1st Floor

AHU-1	2nd Floor Mech	2nd Floor

  - HVAC Control

The HVAC system is controlled by pneumatic thermostats and is connected to the Johnson Controls Metasys System. The rooms are controlled by VAV controllers, which are controlled by room thermostats in each room.

    - Thermostats

All 1st floor AHU’s are controlled by pneumatic thermostats, 2nd floor has VAV capabilities with reheat. The 2nd floor VAV’s are controlled by electronic thermostats which are tied into the Johnson Controls Metasys System.

    - Set Points

Set points are non-adjustable at the thermostat, but are set in the Johnson Controls Metasys System.

    - Unoccupied Temperature Setback

These units are not equipped with any unoccupied features since they run 24hrs/day, 7 days/week.

    - Deck Control

These units are not equipped with hot deck/cold deck control, but do have VAV capabilities.

  - Chilled Water Supply

The building is cooled with chilled water, supplied by the Central Steam Plant. There is a lead/lag pump system for circulating the chilled water system to the air handling units. The pumps are controlled by variable speed drives using the differential pressure of the chilled water loop as the control variable.

  - Heating Water Supply

The building is heated with steam provided by the Central Steam Plant. A reset schedule for the VAV reheat is based on outside air temp is utilized for energy efficiency. This schedule ranges from 110 degf at 80 degf outside, to 180 degf at 10 degf outside air.

  - Special Operations/Instructions

This building is served by the main Generator bank, which supplies power during power outages and during peak shaving.