- PURPOSE

The purpose of this plan is to optimize energy conservation while maintaining adequately conditioned space.

- HVAC OPERATING SCHEDULE

The following schedule represents the time that each air-handling unit (AHU) shall condition its corresponding space:

AHU	SCHEDULE

All	** 24hrs/day, 7 days/week **

- ENERGY OPERATING DESCRIPTION

  - Magnetic Resonance Imaging – Description

The Magnetic Resonance Imaging building houses the Magnetic Resonance Imaging equipment, and is leased to Pitt Memorial Hospital. The building is approximately 8,710 sq ft and is served by 2 air handling units. There is also 1 additional steam space heater.

  - HVAC Supply

AHU#		Location 		Area Served

AHU-1	MRI Mech Room	Magnet Area

AHU-2	MRI Mech Room	Offices & Waiting Area

  - HVAC Control

The HVAC system is controlled by pneumatic thermostats and is not currently connected to the Johnson Controls Metasys System.

    - Thermostats

All AHU’s are controlled by pneumatic thermostats, which are located in the controlled and conditioned area.

    - Set Points

Set points are adjustable at the pneumatic thermostat.

    - Unoccupied Temperature Setback

These units are not equipped with any unoccupied features since they run 24hrs/day, 7 days/week.

    - Deck Control

These units are not equipped with hot deck/cold deck control, but have VAV capabilities.

  - Chilled Water Supply

The building is cooled with chilled water, supplied by the Central Steam Plant. There is a lead/lag pump system for circulating the chilled water system to the air handling units. The pumps are controlled by variable speed drives using the differential pressure of the chilled water loop as the control variable.

  - Heating Water Supply

The building is heated with steam provided by the Central Steam Plant.

  - Special Operations/Instructions

This building is served by the main Generator bank, which supplies power during power outages and during peak shaving.