- PURPOSE

The purpose of this plan is to optimize energy conservation while maintaining adequately conditioned space.

- HVAC OPERATING SCHEDULE

The following schedule represents the time that each air-handling unit (AHU) shall condition its corresponding space:

AHU	SCHEDULE

All	** 24hrs/day, 7 days/week **

- ENERGY OPERATING DESCRIPTION

  - Central Steam Plant – Description

The Central Steam Plant building supplies all of the Health Sciences Campus steam and chilled water. The building is approximately 28,535 sq ft and is served by 1 air-handling unit. There are also 7 additional steam space heaters.

  - HVAC Supply

AHU#		Location 		Area Served

AHU-1	Chiller Room		Steam Plant Area

  - HVAC Control

The HVAC system is controlled by pneumatic thermostats and is not currently connected to the Johnson Controls Metasys System. The unit provides constant volume airflow with steam reheat.

    - Thermostats

All AHU’s are controlled by pneumatic thermostats, which are located in the controlled and conditioned area.

    - Set Points

Set points are adjustable at the pneumatic thermostat.

    - Unoccupied Temperature Setback

These units are not equipped with any unoccupied features since they run 24hrs/day, 7 days/week.

    - Deck Control

These units are not equipped with hot deck/cold deck control.

  - Chilled Water Supply

The building is cooled with chilled water, supplied by the following chiller system: one 200 ton York chiller, one 1200 ton Trane chiller, one 1000 ton Carrier chiller, and two 1000 ton Trane chillers. These chillers are sequenced according to the demand of the system. There is a lead/lag pump system for circulating the chilled water system to the air-handling units. The pumps are controlled by variable speed drives using the differential pressure of the chilled water loop as the control variable.

  - Heating Water Supply

The building is heated with steam provided by 3 (20,000 lb, 150 HP) boilers – 1 Johnston Boiler, 1 Kewanee Boiler, and 1 Superior Boiler.

  - Special Operations/Instructions

This building is served by the main Generator bank, which supplies power during power outages and during peak shaving.