- PURPOSE

The purpose of this plan is to optimize energy conservation while maintaining adequately conditioned space.

- HVAC OPERATING SCHEDULE

The following schedule represents the time that each air-handling unit (AHU) shall condition its corresponding space:

AHU	SCHEDULE

All	** 24hrs/day, 7 days/week **

- ENERGY OPERATING DESCRIPTION

  - West Research Campus – Description

The West Research Campus building is a single story building, which currently houses the Physician’s Assistant Program and the Agrimedicine Program. The building is approximately 21,531 sq ft and is served by 2 air handling units. There are also 3 additional steam space heaters.

  - HVAC Supply

AHU#		Location 		Area Served

AHU-1	Mech Room		North Side Offices

AHU-2	Mech Room		South Side Offices

  - HVAC Control

The HVAC system is controlled by pneumatic thermostats and is not currently connected to the Johnson Controls Metasys System.

    - Thermostats

All AHU’s are controlled by pneumatic thermostats, which are located in the controlled and conditioned area.

    - Set Points

Set points are adjustable at the pneumatic thermostat.

    - Unoccupied Temperature Setback

These units are not equipped with any unoccupied features since they run 24hrs/day, 7 days/week.

    - Deck Control

AHU-1 is equipped with hot deck/cold deck control. AHU-2 is not equipped with hot deck/cold deck control, but has VAV capabilities.

  - Chilled Water Supply

The building is cooled with chilled water, supplied by two 90-ton Carrier chillers.

  - Heating Water Supply

The building is heated with steam provided by 2 1,000,000 BTU boilers. A reset schedule for the VAV reheat is based on outside air temp is utilized for energy efficiency. This schedule ranges from 110 degf at 80 degf outside, to 180 degf at 10 degf outside air.

  - Special Operations/Instructions

This building is served by a Generator, which supplies power during power outages and during peak shaving.