- PURPOSE

The purpose of this plan is to optimize energy conservation while maintaining adequately conditioned space.

- SYSTEM DESCRIPTION

The Malene G Irons Building DEC is a single story clinic and office building.  The HVAC system consists of one air-handler, an air-cooled chiller and stand-alone gas boiler.  The heating and cooling is a two-pipe system with one cooling and one heating system.

- AIR HANDLING UNITS

AHU#	RM#	Area Supplied	Area Description

AHU-1	mechanical	1st floor	waiting & childcare

- HVAC CONTROLS

  - SEQUENCE OF OPERATION

The HVAC system is controlled by an Invensys DMS and monitored on the Ultavist control system.

    - AHU-1   is straight path air-handler with a hot water and chill water coils.

    - The AHU is equipped with minimum outdoor air with a freezestat for freeze protection.

    - The AHU is equipped with fire alarm protection to shut down unit in case of an alarm.

    - When the outdoor temperature is 65-degrees or warmer the cooling is enabled.  When the outdoor air temperature is below 55 degrees the heating system is enabled.  There are times of the year these temperatures need to be adjusted to maintain building temperatures. (Due to the two-pipe configuration of the HVAC system.)

    - Fan coils with independent controls condition the offices and restroom.

  - LOAD MANAGEMENT

There is no load management system for this building.

- COOLING SYSTEM

The building is cooled with an air-cooled McQuay chiller.  On rise of outdoor air temperature the BAS starts the chill water pumps and enables the chiller.  The chiller takes control of the chill water system at this point and maintains 44-degree supply water.

- HEATING SYSTEM

A gas boiler supplies the hot water for heating the building.  The BAS adjusts the temperature reset based on outdoor air temperature.

- SPECIAL OPERATING INSTRUCTIONS