- PURPOSE

The purpose of this plan is to optimize energy conservation while maintaining adequately conditioned space.

- SYSTEM DESCRIPTION

The Jenkins Fine Arts Center is a three-story classroom building served by six air-handlers.  The system utilizes a four-pipe system with an air-cooled chiller and tube and shell heat exchanger.

- AIR HANDLING UNITS

AHU#	RM#	Area Supplied	Area Description

AHU-1	1ST floor mechanical	east	offices & classrooms

AHU-2	2nd floor mechanical	west	offices & classrooms

AHU-3	roof top	2nd floor	classrooms

AHU-4	rooftop	main gallery	art gallery

AHU-5	workroom	senior gallery	art gallery

AHU-6	rooftop	jewelry lab	2 lab areas

- HVAC CONTROLS

  - SEQUENCE OF OPERATION

The HVAC system is controlled by an Invensys DMS-3500 system, connected to the Ethernet and an Ultivist operator workstation at the Steam Plant for control and alarm monitoring.

    - AHU1 & 2 are constant pressure air-handlers.  They incorporate a chill water and hot water coil to maintain temperature to supply the VAV boxes.

    - Minimum fresh air is introduced between 60 degrees and 90 degrees.

    - Each air-handler is equipped with freeze protection and fire protection to stop the blowers and close the outdoor dampers.

    - Cold decks on the air-handlers are on outdoor air reset for energy savings.

    - Pneumatic thermostats control these VAV boxes.  (Boxes cannot be accessed due to asbestos in the ceiling.)

    - AHU-5 is a ceiling mount split system with a hot water coil.

    - AHU-4 is a rooftop package unit with a steam reheat coil, dehumidification and humidification capability.

  - LOAD MANAGEMENT

The chill water system resets supply water temperature on load shed.  This reset is 2 degrees higher before 4:00pm and 4 degrees higher after 4:00pm.

- COOLING SYSTEM

The building is cooled with chill water using a McQuay air-cooled screw chiller.  Two chill water pumps located in the 1st floor mechanical room circulate the chilled water.

- HEATING SYSTEM

A tube and shell converter provides hot water to heat and reheat with a circulator pump staged by outdoor air temperature.  The BAS adjusts the temperature reset based on outdoor air temperature.

- SPECIAL OPERATING INSTRUCTIONS