- PURPOSE

The purpose of this plan is to optimize energy conservation while maintaining adequately conditioned space.

- SYSTEM DESCRIPTION

The Joyner Library is a four story building, divided into two sections, one primarily library and one classrooms and broadcast studios.  The building is approximately 280,00 sq ft served by 28 air-handling units.  The building’s chilled and heating hot water circulates using a four pipe system with one chilled water system and three heating hot water systems.

- AIR HANDLING UNITS

HVAC Supply

AHU#	RM#	Area Supplied	Area Description

1         Basement	Basement file room	File storage area (mech room)

2	2911	2nd Floor	Main office & conference room

3	2911	2nd Floor	offices 1st & 2nd floor

4	2911	2nd Floor	1st floor offices

5	Roof	Special Collections	offices, sitting room & library

6	3904	3rd Floor	N.C. Collections & library

7	1909	1st Floor Drum	offices, filing area & back dock

8	2904	2nd Floor Drum	library & study rooms

9	1904	1st Floor Center	lobby, help desk & offices

10	2907	2nd Floor Center	Library

11	3907	3rd Floor Center	Library

13	Tele.	Telecommunications	Computer room

14	Tele.	Telecommunications (backup)	Computer room

15	98		1st Floor East 	1ST floor offices

16				Basement East 	offices

17	297  	2nd Floor East	Classrooms

18	203	2nd Floor	Classrooms

19				2nd Floor East	Classrooms

20	203	2nd Floor	Auditorium

B1       Main Mech 	Basement	Center Library

E1	B906	Basement West	Periodicals

E2	Mech.	Basement West	Periodicals

E3	1905	1st Floor West	Library (offices)

E4	1908	1st Floor West	Library

E5	2900	2nd Floor West	Library (offices)

E6	2903	2nd Floor West	Library

E7	3900	3rd Floor West	Library

E8	3903	3rd Floor West	Library

- HVAC CONTROLS

  - SEQUENCE OF OPERATION

HVAC Control

The HVAC system is controlled by an Invensys Ultavist control system

    - Thermostats:

AHU#2 is controlled by pneumatic thermostats and set in each area.  All other areas are controlled by the BAS system using zone sensors.

    - Set points:

Set points are 73 degrees in all areas except telecommunications, which is 71 degrees.

    - Unoccupied Temperature Setback:

Due to long operating hours and humidity control no setbacks are used.

    - Deck Control:

Deck control for hot decks is on reset based on building load on AHU 2 –AHU 11.

  - LOAD MANAGEMENT

- COOLING SYSTEM

The building is cooled with chilled water, using two Trane screw chillers.  The system is a glycol primary and chilled water secondary system due to ice storage capabilities.  There is a lead/lag pump system for circulating the chilled water to the air handling units and also a split arm pump, to allow for backup, for the glycol system for AHU#5 and #6.

- HEATING SYSTEM

The building heating hot water is provided by a 3 steam/water heat exchangers, with the supply water temperature on a reset schedule based on outside air temperature.  The campus steam plant provides the steam.  Each of the three heating hot water systems has a dedicated circulator pump.  The systems are located in the west wing basement, main mechanical room and east wing basement.

- SPECIAL OPERATING INSTRUCTIONS

  - Air handling unit #13 serves the Telecommunication room, which is temperature sensitive, and requires constant temperatures.  This system has a backup, system 14, which is a DX unit that is connected to the emergency power system.

  - Return air humidity is monitored and controlled by the BAS system.  Humidity is generated by steam generator (SG-1) and sent to AHU’s 4,5,6,7,8,9,10,11, and basement.  The humidity is injected into the air stream of each unit and controlled by the return air humidity sensor.