- PURPOSE

The purpose of this plan is to optimize energy conservation while maintaining adequately conditioned space.

- SYSTEM DESCRIPTION

The Minges Coliseum is a combination sports arena, classroom, indoor pool and office building.  There are 9 air-handling units that utilize a four pipe chilled water and hot water system, two split system DX units and 6 DX cooling and hot water heat units.  There are three chillers and three steam converters to provide conditioning to the building.

- AIR HANDLING UNITS

AHU#	RM#	Area Supplied	Area Description

1	south mechanical 	bowl	basketball arena

2	south mechanical	south	restroom, locker rooms

3	north mechanical	bowl	basketball arena

4	north mechanical	north	restrooms, classroom

5	east mezzanine	east	restrooms, ticket office

6	west mezzanine	west	restrooms,deans office area

Pool 1	penthouse	pool 	indoor pool

Pool 2	penthouse	showers	locker rooms

W1	A22		office	east corridor offices

W2	A22		conference rm	east conference room

W6	R149	offices	west corridor offices

W7	R169A	offices	north outside offices

W8	R169A	offices	north inside offices

W9	R193	racquetball	racquetball courts

W13	R149	classrooms	south corridor classrooms

Pool 3	top of pool office	office 	pool offices

Pool 4	Room 180	office	south corridor office 180

- HVAC CONTROLS

  - SEQUENCE OF OPERATION

HVAC Control

The HVAC system is controlled by Johnson Metasys system. The chillers are controlled by an Invensys DMS system and monitored by the Ultavist control system.

    - Air-handlers 1-6, pool 1 and pool 2 are controlled by the Metasys system.

    - AHU 2,4,5 & 6 supply VAV boxes that care controlled by the Metasys system.

    - Each VAV box has its own controls located in the space it conditions.

    - AHU 1 & 2 are single path air handlers with both space and return air sensors.

  - LOAD MANAGEMENT

The chill water system resets supply water temperature on load shed.  This reset is 2 degrees higher before 4:00pm and 4 degrees higher after 4:00pm.  The 6 air-handlers controlled by the Metasys system are on schedule to shut down during unoccupied hours.

- COOLING SYSTEM

The building is cooled with three Trane chillers. The chill water pumps are started and the chillers enabled by outdoor air or as needed.

- HEATING SYSTEM

Two tube and shell converters provides the heat for the hot water heat with a circulator pump staged by outdoor air temperature.  Temperature reset is utilized based on outdoor air temperature.  The third tube and shell converter heats water to heat the domestic hot water and the heat for the swimming pool and the dive pool.

- SPECIAL OPERATING INSTRUCTIONS