- PURPOSE

The purpose of this plan is to optimize energy conservation while maintaining adequately conditioned space.

- SYSTEM DESCRIPTION

Mendenhall Student Center is a four-story multipurpose, dining and office building.  The HVAC system consists of multi-zone air-handlers, single path air-handlers, two chillers and two tube and shell hot water converters.  The heating and cooling is a four-pipe system with two cooling and two heating systems.

- AIR HANDLING UNITS

AHU#	RM#	Area Supplied	Area Description

AHU-1	basement ceiling	lobby/radio 	common/radio station

AHU-2	basement hall ceiling	1st floor	radio/transit office

AHU-3	basement hall ceiling	1st floor	radio/transit office

AHU-4	2nd floor mechanical	2nd floor	cafeteria

AHU-5	above kitchen ceiling	kitchen	dishwasher

AHU-6	above kitchen ceiling	kitchen	cooler

AHU-7	above kitchen ceiling	serving area	cafeteria

AHU-8	above dining office	dining	cafeteria

AHU-9	2nd floor ceiling (galley)	galley	kitchen

AHU-10	3rd floor storage ceiling	great room 3	banquet

AHU-11	3rd floor ceiling (men’s rm)	great room 3	banquet

AHU-12	3rd floor ceiling  	great room 2	banquet

AHU-13	3rd floor mech (women’s)	great room 1	banquet

AHU-14	3rd floor mechanical	halls	common

AHU-15	3rd floor mechanical	chancellors suite	banquet

AHU-16	3rd floor ceiling	SGA office	office

AHU-17	3rd floor ceiling	SGA office	office

AHU-18	basement NW corner	computer	computer lab

AHU-19	1st floor mechanical	billiard room	game room

AHU-20	basement mechanical	transit 	offices

AHU-21	basement mechanical	bowling alley	game room

AHU-22	basement mechanical	bank/reading	office & common

AHU-23	2nd floor south mechanical	Spot	snack bar

AHU-24	2nd floor SW mechanical	lobby/multi	common

AHU-25	3rd floor NW mechanical	theatre	theatre

AHU-26	3rd floor NW mechanical	rm 201, 214	office/common

AHU-27	3rd floor SW mechanical	rm 221, 236	office/common

AHU-28	3rd floor south	rm 242	conference room

- HVAC CONTROLS

  - SEQUENCE OF OPERATION

The HVAC system is controlled by an Invensys DMS control system and monitored by the Ultivist control system.

    - Deck temperature controls are based on outdoor air temperature and/or return air temperature.

    - Each AHU is equipped with minimum outdoor air with preheat and has a freezestat for freeze protection.

    - Each AHU is equipped with fire alarm protection to shut down unit in case of an alarm.

  - LOAD MANAGEMENT

The chill water system resets supply water temperature on load shed.  This reset is 2 degrees higher before 4:00pm and 4 degrees higher after 4:00pm.  Individual zone setback is available for energy savings.

- COOLING SYSTEM

The building is cooled with a Carrier screw chiller and a Carrier air-cooled chiller.  The on rise of outdoor air temperature the BAS starts the chill water pumps and enables the chiller.

- HEATING SYSTEM

Two tube and shell converters provides the hot water for the heat with a circulator pump staged by outdoor air temperature.  The BAS adjusts the temperature reset based on outdoor air temperature.

- SPECIAL OPERATING INSTRUCTIONS