- PURPOSE

The purpose of this plan is to optimize energy conservation while maintaining adequately conditioned space.

- SYSTEM DESCRIPTION

Slay and Umstead Residence Halls are three-story dormitories using common mechanical systems.  The HVAC system is a four-pipe system with fan coils in each room.

- AIR HANDLING UNITS

AHU#	RM#		Area Supplied	Area Description

1		lobby closet - Slay	lobby	common

2		lobby closet - Slay	laundry	laundry

3		lobby closet - Umstead	computer	common

4		lobby closet - Umstead	R/A room	apartment

5		lobby mechanical - Umstead	lobby	common

6		lobby mechanical - Umstead   laundry	laundry

- HVAC CONTROLS

  - SEQUENCE OF OPERATION

The HVAC system is controlled by a Siemens control system connected to a modem for dial up connection via phone lines.

    - The building is cooled with chill water, using an air-cooled chiller located outside of the building.  The chiller and chill water pumps are controlled by the BAS based on outdoor air temperature.

    - A tube and shell converter provides the heat with two circulator pumps staged by outdoor air temperature.  Temperature reset is utilized based on outdoor air temperature. This system is controlled by the BAS.

    - There are 6 air-handling units to condition common area.

    - There are 7 make up air units to condition the air for the rest rooms and hallways.

    - Each room has a stand alone 4 pipe fan coil with electronic controls

  - LOAD MANAGEMENT

There is no load management in this building.

- COOLING SYSTEM

The building is cooled with chill water, using an air-cooled chiller located outside of the building.  The chiller and chill water pumps are controlled by the BAS.

- HEATING SYSTEM

A tube and shell converter provides the reheat for the perimeter heat with two circulator pumps staged by outdoor air temperature.  Temperature reset is utilized based on outdoor air temperature. This system is controlled by the BAS.

- SPECIAL OPERATING INSTRUCTIONS

The chilled water system and the domestic hot water system is monitored by the Invensys DMS building automation system and sent to the steam plant via Ethernet and alarms are monitored on the Ultavist system.