- PURPOSE

The purpose of this plan is to optimize energy conservation while maintaining adequately conditioned space.

- SYSTEM DESCRIPTION

The Student Recreation Center is a two-story recreation building, which includes weight room, basketball courts and swimming pool.  The HVAC system consists of 5 single path air-handlers, two centrifugal chillers and a tube and shell hot water converter.  The heating and cooling is a four-pipe system with one cooling and one heating system.

- AIR HANDLING UNITS

AHU#	RM#	Area Supplied	Area Description

AHU-1	north mechanical	north building	offices

AHU-2	north mechanical	north building	offices

AHU-3	west mechanical	1st & 2nd floor	weight room & aerobics

AHU-4	east mechanical	pool	indoor swimming pool

AHU-5	east mechanical	court	basketball courts

- HVAC CONTROLS

  - SEQUENCE OF OPERATION

The HVAC system is controlled by a Siemens control system.

    - AHU-1, 2 & 3 are single path air-handlers that supply VAV boxes with reheat.

    - AHU-4 conditions and dehumidifies the indoor swimming pool.

    - AHU-5 conditions and dehumidifies the basketball courts.

    - Each AHU is equipped with minimum outdoor air with preheat and has a freezestat for freeze protection.

    - Each AHU is equipped with fire alarm protection to shut down unit in case of an alarm.

  - LOAD MANAGEMENT

The chill water system resets supply water temperature on load shed.  This reset is 2 degrees higher before 4:00pm and 4 degrees higher after 4:00pm.  Room temperature setback is utilized on a schedule.  This schedule is changed depending on building usage and communicated to the HVAC Control Shop.

- COOLING SYSTEM

The building is cooled with two Trane Centrifugal chillers.  On the rise of outdoor air temperature the BAS starts the chill water pumps and enables the chiller.  When the chiller sees the load it starts the condenser pumps, enables the cooling tower and starts the chiller.

- HEATING SYSTEM

A tube and shell converter provides hot water for heat with a circulator pump staged by outdoor air temperature.  The BAS adjusts the temperature reset based on outdoor air temperature.

- SPECIAL OPERATING INSTRUCTIONS

Maintaining differential static pressure between the courts and the pool is critical for the dehumidification systems to maintain setpoint.