- PURPOSE

The purpose of this plan is to optimize energy conservation while maintaining adequately conditioned space.

- SYSTEM DESCRIPTION

The Student Health Center is a two-story clinic and office building served by four air-handlers.  The system utilizes a four-pipe system with an air-cooled chiller and tube and shell heat exchanger.

- AIR HANDLING UNITS

AHU#	RM#	Area Supplied	Area Description

AHU-1	mechanical room 194	addition	offices and clinic

AHU-2	mechanical room 108	1st floor north	offices and clinic

AHU-3	mechanical room 227	2nd floor	classroom

AHU-4	mechanical room 213	2nd floor 	offices

- HVAC CONTROLS

  - SEQUENCE OF OPERATION

The HVAC system is controlled by an Invensys DMS-3500 system and Invensys MiroNet system, connected to the Ethernet and an Ultivist operator workstation at the Steam Plant for control and alarm monitoring.

    - AHU1 is constant pressure air-handler.  It incorporates a chill water and hot water coil to maintain temperature to supply the VAV boxes.  Each VAV box has a reheat coil and independent control connected to the BAS system.

    - Minimum fresh air is introduced between 60 degrees and 90 degrees.

    - Each air-handler is equipped with freeze protection and fire protection to stop the blowers and close the outdoor dampers.

    - Cold decks on the air-handlers are on outdoor air reset for energy savings.

  - LOAD MANAGEMENT

The chill water system resets supply water temperature on load shed.  This reset is 2 degrees higher before 4:00pm and 4 degrees higher after 4:00pm.  Temperature reset and air-handler shut down schedules are utilized in this building.

- COOLING SYSTEM

The building is cooled with chill water using a Trane air-cooled screw chiller.  The chill water pump is located in the 1st floor mechanical room circulate the chilled water.

- HEATING SYSTEM

A tube and shell converter provides the hot water for the heat with a circulator pump staged by outdoor air temperature.  The BAS adjusts the temperature reset based on outdoor air temperature.

- SPECIAL OPERATING INSTRUCTIONS