- PURPOSE

The purpose of this plan is to optimize energy conservation while maintaining adequately conditioned space.

- SYSTEM DESCRIPTION

Todd Dining Hall is a single story building with a kitchen, dining hall, banquet hall and offices.  Six air-handling units condition the space.  The building’s chill water and hot water system uses a four-pipe system with one chilled water system and one hot water system.

- AIR HANDLING UNITS

AHU#	RM#	Area Supplied

AHU-1.	1ST floor mech. Rm.	Serving area

AHU-2A	1ST floor mech. Rm.	Sweethearts

AHU-2B	1ST floor mech. Rm.	Sweethearts

AHU-3	Roof mech. Rm.	kitchen

AHU-4	Roof mech. Rm.	East dining

AHU-5	Roof mech. Rm.	North dining

- HVAC CONTROLS

  - SEQUENCE OF OPERATION

A Siemen’s System 600, with dial up capabilities, controls the HVAC system.  We also monitor the chiller temperatures and alarms through the Invensys DMS-3500 system.

    - AHU-1, 3, 4  & 5 have hot water and chill water coils and temper the air to maintain zone temperature.  Each unit has outside make up air; freeze protections and fire alarm shutdown.  These units are controlled by the building BAS.

    - AHU-2A & 2B serve the banquet area and share a common return.  Fresh air is mixed in the common return.  Freeze and fire protection is on each of these units for shut down. These units are controlled by the BAS.

    - A zone thermostat and humidistat is in each zone to control the air-handlers.

    - The kitchen has exhaust hoods with fresh air makeup fans (with gas preheat) to keep the building static positive. The kitchen fans are not controlled by the BAS.

    - The offices have an independent rooftop unit to condition the space.  This system is self-contained and is not on the BAS.

    - The main dining area has electric baseboard heat with each heater having it own control.

  - LOAD MANAGEMENT

Building is on setback schedule but no other load management at this time.

- COOLING SYSTEM

The building is cooled with chill water using a Trane air-cooled chiller located outside of the building.  The chiller and chill water pumps are controlled by the BAS.

- HEATING SYSTEM

A tube and shell converter provides the hot water for the heating with a circulator pump staged by outdoor air temperature.  The BAS adjusts the temperature reset based on outdoor air temperature.

- SPECIAL OPERATING INSTRUCTIONS