- PURPOSE

The purpose of this plan is to optimize energy conservation while maintaining adequately conditioned space.

- SYSTEM DESCRIPTION

The Whichard Building is a two-story office building.  The HVAC system consists of four multi-zone air-handlers and two single path air-handlers, a McQuay air-cooled chiller and tube and shell hot water converter.  The heating and cooling is a four-pipe system with one cooling and one heating system.

- AIR HANDLING UNITS

AHU#	RM#	Area Supplied	Area Description

AHU-1	2nd floor closet	2nd floor annex	offices

AHU-2	1st floor closet	1st floor annex	offices

AHU-3	1st floor mechanical	1st floor	offices

AHU-4	2nd floor north	2nd floor	offices

AHU-5	2nd floor south	2nd floor	offices

AHU-6	mechanical	1st floor south	offices

- HVAC CONTROLS

  - SEQUENCE OF OPERATION

The chiller system is controlled by an Invensys DMS control system and monitored by the Ultavist control system.

    - AHU-1, 2, 6 & 7 are multi-zone air-handlers with a hot water and chill water coils.

    - AHU-4, & 5 are single path air handlers with hot water and chill water coils.

    - Pneumatic thermostats control each zone of the multi-zone air handlers while the single path air-handlers have pneumatic thermostats.

    - Deck temperature controls are based on outdoor air temperature and/or return air temperature.

  - LOAD MANAGEMENT

There is no load management on this building.

- COOLING SYSTEM

The building is cooled with a McQuay air-cooled chiller.  On the rise of outdoor air temperature the BAS starts the chill water pumps and enables the chiller.

- HEATING SYSTEM

A tube and shell converter provides hot water for heat with a circulator pump staged by outdoor air temperature.

- SPECIAL OPERATING INSTRUCTIONS