- PURPOSE

The purpose of this plan is to optimize energy conservation while maintaining adequately conditioned space.

- SYSTEM DESCRIPTION

The Wright Building is a multi use building with an auditorium, offices, meeting rooms, snack shop and bookstore.  The HVAC system utilizes a four-pipe system using a screw chiller and steam heat.

- AIR HANDLING UNITS

AHU#	RM#	Area Supplied	Area Description

1		upstairs mechanical	ROTC	office & dressing rooms

2A		south side of stairs	offices	counseling center

2B		above auditorium	auditorium	auditorium

3		above auditorium	auditorium	auditorium

4		storage		south lobby	lobby

5		storage		north lobby	lobby

6		storage		bookstore	bookstore

7		north side of office	offices	offices

8		storage		kitchen	kitchen & serving

9		storage		dining	dining room

10		warehouse	warehouse	storage

11		storage 2nd floor 	offices 	2nd floor west offices

12		outside mechanical	dining	dining room

- HVAC CONTROLS

  - SEQUENCE OF OPERATION

The HVAC system is controlled by an Invensys DMS-3500 system, connected to the Ethernet.

    - AHU 4 & 5 are chill water-cooling and electric heat while the remainder of the AHU’s use steam heat.

    - AHU’s 2, 3, 4, 5 and 12 are controlled by the BAS.

  - LOAD MANAGEMENT

There is no load management on this building.

- COOLING SYSTEM

The building is cooled with a variable speed York centrifugal chiller.  On rise of outdoor air temperature the BAS starts the chill water pumps and enables the chiller.  When the chiller see the load it starts the condenser pumps, enables the cooling tower and starts the chiller.

- HEATING SYSTEM

The heating is primarily steam heat throughout the building.

- SPECIAL OPERATING INSTRUCTIONS