# GENERAL

The Main Campus Steam Plant must maintain a fuel oil inventory.  The full capacity of the Main Campus Steam Plant fuel oil inventory is                                    300,000 gals. The amount on-hand is a balance between having adequate seasonal supplies in case of natural gas curtailment and the economics of natural gas and fuel oil prices.  This FSSP provides guidelines for maintaining that inventory.

## RESPONSIBILITIES

  - The Steam Plant Supervisor has overall responsibility for maintaining the fuel oil inventory.

  - Based on fluctuations in natural gas and fuel oil prices, the Senior Associate Vice Chancellor for Campus Operations may issue directives to vary from the routine practice.

## PROCEDURE

  - Routine Practice

    - The Heating Plant will normally begin the heating season with the fuel oil tanks filled with approximately 300,000 gals. of fuel oil.  This is a 19-day heating season supply of fuel oil at a use rate of 14,000 gals/day and a 39,000 gal. heel.

    - Once curtailment begins, no fuel oil will be replaced until the inventory reaches a nominal 10-day heating season supply (179,000 gals.) This will insure that the University has a sufficient supply of fuel oil in the event of extended severe weather and possible fuel oil delivery problems.  At that level, as a tanker load of fuel oil is burned, it will be replaced.

    - Beginning March, the Heating Plant will lower the reorder point to approximately 109,000 gals. This is a 10-day spring/summer supply of fuel oil at a use rate of 7,000  gals/day and a 39,000 gal. heel. At that level, as a tanker load of fuel oil is burned, it will be replaced.

    - Beginning April, the Heating Plant will lower the reorder point to approximately 74,000 gals. This is a 5-day spring/summer supply of fuel oil at a use rate of 7,000 gals/day and a 39,000 gal. heel. At that level, as a tanker load of fuel oil is burned, it will be replaced.

    - Normally the tanks will be refilled in May/June when fuel oil prices are at their lowest.  Fuel oil and natural gas prices are usually at their lowest during this time and at their highest at the peak of the heating season.  A savings is realized whenever the tanks are filled during a period of low prices and the same inventory is used during a period of peak prices.  If the decision is made to refill using the current Fiscal Year budget, then it is important that the tanks be refilled in May or as early in June as possible to insure that all invoices are received and processed before the end of the fiscal year.  In the past, fuel oil companies have not responded well to rush demands for invoices.

IMPORTANT:  The actual decision to begin end-of-year refill will come from the Senior Associate Vice Chancellor for Campus Operations.

    - Each month each boiler shall operate on both #2 fuel oil and natural gas to ensure equipment readiness and operator familiarity.

      - If the boilers are operating on natural gas then the Steam Plant Supervisor shall initiate a work order to switch each boiler to #2 fuel oil during the month.  The boilers should operate on #2 fuel oil long enough to determine if all systems are operational.

      - If the boilers are operating on #2 fuel oil during the month, then routine carbon burn-off procedures will require that each boiler be switched to natural gas at least once a month.

      - Since Campus Operations commits to consumption levels of natural gas on a monthly basis, the switch from natural gas to #2 fuel oil should be initiated at the beginning of the month.  Thus, if the natural gas consumption level maximum is reached requiring the boilers to be switched to #2 fuel oil, the boilers will have been checked for operating with #2 fuel oil before a switch is required.

      - To ensure operator familiarity, the Steam Plant Supervisor shall schedule the switch to ensure that each boiler operator conducts a switch during a three month period.

      - When the price of the alternate fuel is significant, the Steam Plant Supervisor should minimize the amount of fuel consumed during the switch.

  - Because fuel prices can have a significant impact on the budget, the Senior Associate Vice Chancellor for Campus Operations should be notified of any plans to vary from the routine practice.

  - Due to fluctuations in fuel oil and natural gas prices, the Senior Associate Vice Chancellor for Campus Operations may direct a variance from the above routine practice.  This direction will normally come through the Director, Resource Management – Campus Operations by email to the Steam Plant Supervisor and cc to Executive Director, Facilities Services – Main Campus and Assistant Director, Utilities Services. The Steam Plant Supervisor will take the necessary action and confirm action by email to Director, Resource Management – Campus Operations and cc to Executive Director, Facilities Services – Main Campus and Assistant Director, Utilities Services.